## Cover Page
Community Tap stand(CTS) Project to be constructed in Namulo community in Butaleja District
Blank BOQ Estimates

## Summary
Community Tap stand (CTS) Project to be constructed in Namulo Community Butaleja District
NOTE: 1. GOAL shall be constructing 2No Community Tap Stands, (CTS) in Butaleja District - Eastern Uganda. These are conversions (Already existing handpumps that shall be motorised). 2. This unpriced Bill of Quantities is for One CTS only 3. The currency shall be in Uganda Shillings (UGX)
GRAND SUMMARY
ITEM NO. | DESCRIPTION | AMOUNT (UGX)
1 | BOREHOLE AND PUMP HOUSE | 0
2 | RESERVOIR/TANK | 0
3 | ELECTROMECHANICAL | 0
4 | DISTRIBUTION | 0
| SUB-TOTAL 1 | 0
| ADD 18% VAT | 0
| GRAND TOTAL | 0

## Borehole and Pump House
Community Tap stand(CTS) Project to be constructed in Namulo Community in Butaleja District.
BILL NO. 1 BOREHOLE AND PUMP HOUSE
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
BOREHOLES AND PUMP HOUSE
Galvanised Mild Steel (GMS) pipes with threaded joints, all to BS 3601, not in trench and of the following sizes: (Transmission line and Wash out)
1.1.1 | 50mm(2") ND Transmision line | m | 10 |  | 0
1.1.2 | 50mm(2") ND for Pump wash out | m | 3 |  | 0
1.1.3 | GMS double socketed long radius 90 degrees bends to BS 3601 of 50mm(2") ND | nr | 1 |  | 0
1.1.4 | GMS socketed bends 45 degrees 50(2")mm ND | nr | 1 |  | 0
1.1.5 | Double socketed brasss gate valves to BS 5150 for operation by hand, to ND 50 mm(2") | nr | 2 |  | 0
1.1.6 | Socketed GMS Non-Return Valve to ISO 2441 to PN 10 for ND 50mm(2") | nr | 1 |  | 0
1.1.7 | Socketed Pressure Gauge N30 Series for ND 25mm(1") | nr | 1 |  | 0
1.1.8 | Socketed Air valve ND 25mm(1") | nr | 1 |  | 0
1.1.9 | GMS Equal Tee ND 50x50x50mm (2x2x2") | nr | 1 |  | 0
1.1.10 | GMS Reducing Tee ND 50X50X25mm(2x2x1") | nr | 2 |  | 0
1.1.11 | GMS Reducing Socket ND50x40mm(2X1½") | nr | 1 |  | 0
1.1.12 | GMS ND 5Omm(2") Nipple | nr | 6 |  | 0
1.1.13 | GMS ND 40mm(1½") Nipple | nr | 1 |  | 0
1.1.14 | GMS ND 25mm(1") Nipple | nr | 1 |  | 0
1.1.15 | GMS ND50mm(2") socketed union | nr | 1 |  | 0
1.1.16 | GMS ND 50mm(2") Elbow | nr | 2 |  | 0
1.1.17 | GMS ND 50mm(2") Soceket | nr | 3 |  | 0
1.1.18 | Supply,Install and do Welding of the third plate as well cover for the borehole and all its accessories for the purpose of securing the pump and all installations in the well (the client has the third plate) | nr | 1 |  | 0
BUILDING WORKS
1.1.19 | Construct a chain linked fence; 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of galvanised barbed wire gauge 10 on top, anchored into blockwork dwarf wall as per drawings number 2(Page 2 of 2), height 2.075m. | M | 38 |  | 0
| Construct hollow bricks to close off the open area on the tower, as per attached drawings | m² | 21.9 |  | 0
1.1.20 | Supply and fix gate to BS 3470, painted to Engineer's approval, of 2X2.075M as per attached detailed drawing number 2 (Page 2 of 2), Mild steel plates - 23 of 1mm welded over the existing Pump House door and Provide heavy duty pud lock(Mindy Guard-Medium Size 50mm) for the gate | Item | 1 |  | 0
1.1.21 | Provide and lay machine crushed stone aggregate of size 25mm, at the entrance of the pump house done to specifications and satisifaction of the Engineer | m² | 2.47 |  | 0
1.1.22 | Plant paspalum grass in the compound of pump house/intake and provide watering during time of construction. See detailed drawings number 2( page 1 of 2) | m² | 24.39 |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Reservoir
Community Tap stand(CTS) Project to be constructed in Namulo Community in Butaleja District
BILL NO.2 8000LITRES RESERVOIR/PLASTIC TANKS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
2 | Element NO.1: Substructure
2.1 | Site Preparation
2.1.1 | Excavate over site to reduced levels commencing from stripped site level | m² | 36 |  | 0
2.1.2 | Dig out any existing termite mount, destory queen and apply approved anti-termite spray to the entire site | m² | 81 |  | 0
2.1.3 | Anti- termite treatment to sides and bottoms of foundation | m² | 28 |  | 0
2.1.4 | Ditto but stripped surfaces of the ground | m² | 7.84 |  | 0
2.1.5 | Ditto but blinded surface of hardcore | m² | 7.84 |  | 0
2.2 | Trees |  |  |  | 0
2.2.1 | Cut and dispose of trees of the following girth; include removal of stump |  |  |  | 0
2.2.2 | Girth 500mm - 1000mm (0.5m-1m) | nr | 1 |  | 0
2.2.3 | Girth 1000mm - 2000mm(1m-2m) | nr | 1 |  | 0
2.3 | Stumps |  |  |  | 0
2.3.1 | Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil |  |  |  | 0
2.3.2 | Diameter 150mm - 500mm | nr | 1 |  | 0
2.3.3 | Diameter 500mm - 1m | nr | 1 |  | 0
2.4 | Earthworks and Excavation |  |  |  | 0
2.4.1 | Excavate foundation trench not exceeding 1.5m deep commencing from reduced level | m³ | 7.5 |  | 0
2.4.2 | Ditto but column bases | m³ | 6 |  | 0
2.4.3 | Extra over excavations: breaking up rock met with in excavations | m³ | 0.8 |  | 0
2.5 | Disposal of excavated materials |  |  |  | 0
2.5.1 | Return, fill in and ram selected excavated material around the foundation around foundations and walling; placed in 200mm layers, watered and compacted to 95% MDD | m³ | 8.5 |  | 0
2.5.2 | Load, wheel and evenly spread out surplus soil on site | m³ | 5.8 |  | 0
2.6 | Fillings |  |  |  | 0
2.6.1 | 125mm murram filling: well watered and compacted to 95% MDD 95%: to make up levels under floor bed | m² | 6.6 |  | 0
2.6.2 | 150mm Hardcore bed: in broken stone well compacted, consolidated and blinded with and including 20mmlayer of lake/river sand well watered ready to receive concrete | m² | 6.6 |  | 0
2.6.3 | Ditto: Under splash aprons | m² | 3.996 |  | 0
2.7 | Concrete works |  |  |  | 0
2.7.1 | Mass concrete mix 1:4:8/38mm aggregate; 50mm thick blinding to foundations | m² | 27.25 |  | 0
2.7.2 | Mass concrete mix 1:3:6/20mm aggregate, in foundation trenches | m³ | 2.11 |  | 0
2.7.3 | Reinforced concrete in mix 1:1.5:3/20mm aggregate vibrated in |  |  |  | 0
2.7.4 | Column and Column Base [Plinth Structure] | m³ | 2.25 |  | 0
2.7.5 | Ditto but to Bracing ground beam | m³ | 1.39 |  | 0
2.7.6 | Reinforced concrete in mix 1:3:6/20mm aggregate vibrated in 100mm thick ground floor | m² | 10.87 |  | 0
2.8 | Sawn Form work |  |  |  | 0
2.8.1 | Ditto Slab | m² | 10.87 |  | 0
| ditto to ground beam | m² | 31.27 |  | 0
2.9 | Reinforcement |  |  |  | 0
2.9.1 | Mild steel bar reinforcement to BS 4483 |  |  |  | 0
2.9.2 | Mesh A98 in floor slab weighing 1.58kg/m² | m² | 7.84 |  | 0
2.9.3 | 8mm bars(shear reinforcement to column) | Kg | 48 |  | 0
2.9.4 | 8mm bar as a chair/spacer for the column base | Kg | 2 |  | 0
2.10 | High yield tensile steel bar reinforcement to BS 4461 as described including cutting to lengths, bending, hoisting and fixing including all the ncessary binding wire and chair/ spacer blocks |  |  |  | 0
2.10.1 | 16mm bars | Kg | 170 |  | 0
2.11 | Sawn Form work |  |  |  | 0
2.11.1 | Ditto but Columns | m² | 12 |  | 0
2.12 | Foundation/Plinth Walls |  |  |  | 0
2.12.1 | Hard burnt clay bricks to BS 3921(3.5N/mm² compressive strength) bedded and jointed in cement and sand(1:3) mortar |  |  |  | 0
2.12.2 | 230mm wall | m² | 16.8 |  | 0
2.13 | Damp Proof Membrane |  |  |  | 0
2.13.1 | 1000 Gauge polythene sheet damp proof membrane in one layer with 300mm end laps: laid on blinded hardcore | m² | 6.6 |  | 0
2.13.2 | Horizontal Damp Proof Course(DPC) and Ant Proof Course(APC): hessian based bitumen felt: lapped 150mm on ends laid on cement and sand (1:3) mortar bed. APC average thickness of 25mm |  |  |  | 0
2.13.3 | 230mm wide: APC laid along the main layout of wall | m | 11.2 |  | 0
2.13.4 | DPC | roll | 2 |  | 0
2.14 | Plinth wall finishes |  |  |  | 0
2.14.1 | 15mm cement and sand(1:3) render: steel trowelled smooth | m² | 18.23 |  | 0
2.14.2 | Prepare and apply three coats bituminous or other approved water resistant paint to: rendered plinth wall | m² | 18.23 |  | 0
2.15 | Element NO.2: Building Frame[Super structure] |  |  |  | 0
2.15.1 | Reinforced in-situ concrete mix 1:1.5:3/14-20mm aggregate (machine crush-aggregate) in |  |  |  | 0
2.15.2 | Columns | m³ | 2.05 |  | 0
2.15.3 | Ring beams | m³ | 2.5 |  | 0
2.15.4 | Slab but concrete mix 1:2:4/14-20mm aggregate | m³ | 1.78 |  | 0
2.16 | High yield tensile steel bar reinforcement to BS 4461 as described including cutting to lengths, bending, hoisting and fixing including all the ncessary binding wire and spacer blocks |  |  |  | 0
2.16.1 | 16mm bars for columns and ring beam | Kg | 367.9 |  | 0
2.16.2 | 8mm bars(shear reinforcement to column and beams) | Kg | 257.25 |  | 0
2.16.3 | 10mm bars for slabs | Kg | 74.55 |  | 0
2.17 | Sundries |  |  |  | 0
2.17.1 | Binding wires(2mm diameter) | roll | 1 |  | 0
2.17.2 | Assorted Nails | Kg | 15 |  | 0
2.18 | Sawn Form work to: |  |  |  | 0
2.18.1 | Sides and soffites: Beam | m² | 95.76 |  | 0
2.18.2 | Vertical sides: Column | m² | 88.32 |  | 0
2.18.3 | Soffites: Slab | m² | 9.18 |  | 0
2.19 | Element NO.3: Walls |  |  |  | 0
2.19.1 | Provide Eucalyptus poles (75mm[3"] to 100mm[4"]) in size and length between 15 to 20feet) @) as a temporary structure for scaffolding | No. | 10 |  | 0
2.19.2 | Hard burnt clay bricks to BS 3921(3.5N/mm² compressive strength) bedded and jointed in cement and sand(1:3) mortar |  |  |  | 0
2.19.3 | 230mm Wall | m² | 17 |  | 0
2.19.4 | Square Hollow Section mild steel SHS MS 30x20x2mm, primed with one coat of red oxide primer before fixing: complete with lugs built into wall, see drawings. Spacing of 200mm c/c including cutting and welding, | m | 36 |  | 0
2.19.5 | Concrete: Mass concrete of mix 1:2:4/20mm aggregate; 75mm cast on wall ready to receive RHS MS 30x20x2mm | m³ | 0.07 |  | 0
2.20 | Wall finishes |  |  |  | 0
2.20.1 | Internal Wall |  |  |  | 0
2.20.2 | Cement/lime putty/sand(1:2:9) |  |  |  | 0
2.20.3 | 15mm Plaster to wall: Walls and concrete surfaces: Steel trowelled smooth | m² | 20.14 |  | 0
2.20.4 | Prepare surfaces: apply three coats vinyl silk soft white emulsion paint: on steel trowelled plaster: to |  |  |  | 0
2.20.5 | Walls and concrete surfaces internally | m² | 17 |  | 0
2.20.6 | External Walls |  |  |  | 0
2.20.7 | 12mm cement and sand(1:4) wall rendering in two coats steel trowelled hard and smooth on wall externally | m² | 20.14 |  | 0
2.20.8 | Provide rough cast to external wall. See drawings; cement and sand (1:3) | m² | 17 |  | 0
2.20.9 | Prepare and apply three coats of plastic emulsion paint on rough cast walls externallly | m² | 17 |  | 0
2.20.10 | Ditto but on steel tube grills of 30x20x2mm RHS MS | m² | 62.5 |  | 0
2.20.11 | supply and fix on the wall inside the pump house a lockable cage measuring (1m x0.5m) as housing for the PV Disconnect and Charge Controller for the PV generator | Item | 1 |  | 0
2.21 | Floor Finishes |  |  |  | 0
2.21.1 | 25mm cement and sand (1:4) screed finished smooth | m² | 7.82 |  | 0
2.21.2 | 20x100 mm skirting with rounded top edge and coved at the jucntions with floor screed(mix of 1:3) | m | 12.18 |  | 0
2.21.3 | Prepare and apply three coats of gloss paint on skirting 100-200mm girth | m | 10.28 |  | 0
2.22 | Splash Apron |  |  |  | 0
2.22.1 | 600mmx75mm thick concrete of mix 1:3:6/25mm aggregate with all the necessary brick work and formwork. See drawings | m² | 7.44 |  | 0
2.23 | Door |  |  |  | 0
2.23.1 | Purpose made doors to the Enginer's Details. See detailed in drawings 1(Page 10 of 11). Primed with red oxide paint before delivery to site, painted blue on site complete with and including all the necessary hinges, metallic spikes, lugs and locking devices. Provide a heavy duty pud lock (Mindy Guard-Medium Size 50mm) for the door. | Item | 1 |  | 0
2.24 | Solar Mounting Structure |  |  |  | 0
2.24.1 | Solar Array mounting frame for 4 no. Solar panels each measuring 1956x992mm, to be fabricated using galvanised rust-free/resistant steel metal supported by galvanised steel pipes/angle sections mounted onto a reinforced concrete tower constructed to specifications. Special bolts and nuts with arren-keys shall be supplied for fastening modules, enhanced for theft-proof and spot welded, Ref to drawing nos: GKA [- -]12, RCT-GKA [- -]03 & 04, RCT-GKA [- -]01 & 02 and RCT-GKA [- -] 05) attached. | Item | 1 |  | 0
2.24.2 | Solar Array mounting frame for 10no. Solar panels each measuring 1956x992mm, to be fabricated using galvanised rust-free/resistant steel metal supported by galvanised steel pipes/angle sections onto a reinforced concrete base constructed to specifications. Special bolts and nuts with arren-keys shall be supplied for fastening modules, enhanced for theft-proof and spot welded, Ref drawing attached. | Item | 1 |  | Rate only
2.25 | Water Tank and Plumbing System
2.25.1 | Supply and Install Gentex tank of 8000litres plastic tank with a 0.35m steel wide access man way, ball float valve, fixed inlet (50mm diam), outlet (50mm diam ), overflow and washout (50mm dia)GMS pipes connection complete with internal pipe work and fittings, bracings as detailed in the drawings number 1(Page 3 of 11) | Item | 1 |  | 0
2.25.2 | Supply and fix iron sheet gauge 28 prepainted on the four vertical sides of the tank to protect the tank from sun radiation | m² | 29.84 |  | 0
2.25.3 | Using self-tapping screws of size 8" and its bits and socket, and hand drill, fix the iron sheet on all the four vertical sides of the tank. No iron sheet should be fix with binding wires. Fixing will only be done using self-tapping screws. | m² | 29.84 |  | 0
| Supply of foldable access ladders |  |  |  | 0
| Stainless steel - Material: 304 Stainless Steel or 316 Stainless Steel - width 500mm and height 4000mm | No | 1 |  | 0
2.26 | Supply and fix galvanised Mild Steel (GMS) pipes with threaded joints, all to BS 3601, not in trench and of the following sizes
2.26.1 | 50mm ND drop down pipe | m | 7 |  | 0
2.26.2 | GMS double socketed long radius 90 degrees bends to BS 3601, flanges to ISO 2441 of ND 50mm(2") | nr. | 2 |  | 0
2.26.3 | All socketed gate valves to BS 5150 for operation by hand, to ND 50 mm(2") | nr. | 1 |  | 0
2.26.4 | Socketed nipples ND 50mm(2") | nr. | 2 |  | 0
2.26.5 | Socketed connecting Union/ connector ND50mm(2") | nr. | 2 |  | 0
2.26.6 | HDPE PN6 ND 50mm(2") male adapter | nr. | 1 |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Electro-Mechananical
Community Tap stand(CTS) Project to be constructed in Namulo Community in Butaleja District
BILL NO.3 ELECTROMECHANICAL
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
ELECTRO-MECHANICAL WORKS
Submersible pump
NB. 1. Contractors are to quote for Lorentz pump of PS2-1800C-SJ5-12 series of Max flow rate of 7.6m3/hr and Max.head; total head (H) of 70m; with Controller PS-1800, Max.Power of 1.8KW. During construction. A Pump and PV sizing shall be done and PS2-1800C-SJ5-12 pump that shall be selected for a particular site, shall not exceed the characteristic(Flow rate and Head) mentioned. 2. Further, Contractors are also to quote for Lorentz PV panels of Peak Power (P max) of 600Wp, OR Soleil Power Solar Panels of similar wattage. Maximum number of Solar Panels to be used per site will be 4. 3. The well casing, internal is 5 inches
3.1.1 | Lorentz pump as PS2-1800C-SJ5-12 series Pumpset Q = 7.6m3/hr(Max.), H = 70m(Max.) total head, with controller PS-1800, Max. power of 1.8KW with a high efficiency EC Drive Brushless Motor; Model Lorentz ECDRIVE 1800C-SJ5-12, rated Power 1.8kw and Motor cable of 4mm2 for 35m. (Please check Page 18-19 of 31 of the combined drawings) | nr | 1 |  | 0
ELECTRICAL WORKS
Solar PV System
3.1.2 | 1.Lorentz PV as LC200-Portable Kit Polycrystalline or monocrystalline solar panels, @200Wp, 8.84Imp, 37.3 Vmp, See details in PV and Pump Sizing Report attached OR 2. Soleil power solar panels monocrystalline or Polycrystalline of Module of similar wattage. See details in attached sheets of typical soleil power solar panel data sheets together with the drawings | nr | 3 |  | 0
3.1.3 | PV Disconnect 440 - 40- 1 box connection with DC Disconnect Switch and Lightning surge protection with maximum voltage of 440V and maximum current of 40A, See details in PV and Pump Sizing report |  | 1 |  | 0
3.1.4 | Surge protectors2 (See details in PV & Pump sizing report attached) | nr | 1 |  | 0
0
3.1.5 | Supply and fix a 3G PS-Communicator compartible with PS2 Pumps |  | 1 |  | 0
0
| Float switch (See details in PV & Pump sizing report attached) | nr. | 1 |  | 0
0
3.1.6 | Well Probe V2 ( see details in PV & Pump Sizing report attached) | nr | 1 |  | 0
0
3.1.7 | Assortment of electrical cables, interconnects, concrete nails & Screws and accessories for complete system wiring, including where necessary, underground cables, wired in full conduit technique; supplied and installed to specifications. | sum | 1 |  | 0
0
3.1.8 | Weld to permanent lock of 30x20x2mm angle bars for 8000mm total length as per attached drawings and instruction by GOAL Engineer. The weld shall be completed on all edges not to provide for opening. | LS | 1 |  | 0
0
Wiring, Riser Pipe and Pump Installation
3.1.9 | Motor cable (water resistent Cable),4mm² | m | 0 |  | Rate only
0
3.1.10 | Heavy duty white column Upvc pipes riser pipe ND50mm PN10 of square threads, 6.4mm min. thickness and able to withstand 35kg/sq cm | nr | 7 |  | 0
0
3.1.11 | PPR adaptor set ND50mm(1½") PN10 | set | 2 |  | 0
3.1.12 | Provide a safetyline(A polypropylene rope or a stainless steel braided cable) for future maintenance of the pump | m | 35
| Earthing and Lightening Protection |  |  |  | 0
3.1.13 | Using self-tapping screws of size 8" and its bits and socket, and hand drill, fix the iron sheet on all the four vertical sides of the tank. No iron sheet should be fix with binding wires. Fixing will only be done using self-tapping screws. | nr | 1 |  | 0
0
3.1.14 | Provide a plastic conduit of 32mm for the copper rod. The copper rod should be inserted into the 32mm conduit and fix with the necessary fixing accessories to wall. | m | 11 |  | 0
Water Monitoring system
0
3.1.15 | Bulk Meter, WP Water meter DN50mm(2"), See details in the PV & Pump Sizing report attached (Page 21-23 of 31 of the combined drawings) | nr | 1 |  | 0
0
| Carried to Summary |  |  |  | 0
| Page 1 |  |  |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Distribn
Community Tap stand (CTS) Project to be constructed in Namulo Community in Butaleja District
BILL NO.5 DISTRIBUTION SYSTEM
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
NB: Contractors Should note that there is going to be no provision for construction a a Public Tap stand/Standpipe. Only a meter chamber shall be constructed. Distribution pipe ending after the meter chamber to be fitted with a Female Adapter(PE) and pluged with End Cap(PE)
5.1 | DEMOLITION & SITE CLEARANCE
5.1.1 | General clearance along pipeline | m2 | 214 |  | 0
5.2 | Plastic PE pressure pipes to BS 5114 OR its equivalent, all to PN6 and fittings all to PN 10, laid in trench to adepth n.e 1.5m. Rate should include cost of excavation, laying and backfilling of trench
5.2 | PE Pressure Pipes
5.2.1 | OD50mm | m | 263 |  | 0
5.2.2 | OD40mm | m | 152 |  | 0
5.2.3 | OD63mm | m | 296 |  | 0
5.3 | PE Straight Coupling - PN10
5.3.1 | OD50mm | nr | 1
5.3.2 | OD40mm | nr | 3 |  | 0
5.3.3 | OD63mm | nr | 6 |  | 0
5.4 | PIPEWORK-FITTINGS AND VALVES
5.4.1 | HDPE Tee
Equal Tee - PN6
| 63x63mmOD | nr | 1 |  | 0
5.4.2 | Reducing Tee - PN6
5.4.2.1 | 50x40 mm OD | nr. | 1 |  | 0
5.4.3 | Reducing Connector - PN6
5.4.3.1 | 63x50mmOD | nr | 2
5.4.3.2 | 50X40mm OD | nr. | 2 |  | 0
5.4.4.0 | PE Adaptor
5.4.4.1 | Male Adaptor
5.4.5.1 | 50mmOD | nr | 1 |  | 0
5.4.6.0 | PE End Cap
5.4.6.1 | 40mm OD | nr. | 3 |  | 0
5.5.0 | Air Release Valve
5.5.1 | Supply and install a 40mmOD air release valve with all its fittings,along the PN6 pipeline, well secured by 230mm thick,1000x1000mm masonry manhole, well finished and covered with a reinforced concrete cover cast insitu using 10mm rebars at 150mm spacing, to be constructed in consultation with the GOAL Engineer onsite. | nr. | 1 |  | 0
| Collection 1 to Summary |  |  |  | 0
5.6.1 | Marker post for pipelines as per drawings Number 3 (Page 1 of 1). Painted white and writing painted black | nr. | 4 |  | 0
0
5.6.2 | Construct a reinforced concrete meter chamber with a precast reinforced concrete concrete cover raising above the ground level by 300m as in the drawing number 5 (Page 1 of 1) including all earthwork, concrete works, plumbing, all relevant fitings( Gate Valve, meter,etc.); galvanized iron pipe and fitting all to PN 6 | nr | 3 |  | 0
| Collection 2 to Summary |  |  |  | 0
5.6.1 | Page 1: Collection 1 to Summary |  |  |  | 0
5.6.2 | Page 2: Collection 2 to Summary |  |  |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0