## Cover Page
Community Tap stand(CTS) Project to be constructed in Leteruwa Community in Kaabong District
Blank BOQ Estimates

## Summary
Community Tap stand (CTS) Project to be constructed in Leteruwa Community in Kaabong District
NOTE: 1. GOAL shall be constructing 2No Community Tap Stands, (CTS) in Kaabong District - Northern Uganda. These are conversions (Already existing handpumps that shall be motorised). 2. This unpriced Bill of Quantities is for One CTS only 3. The currency shall be in Uganda Shillings (UGX)
GRAND SUMMARY
ITEM NO. | DESCRIPTION | AMOUNT (USHS.)
1 | BOREHOLE AND BOREHOLE SOURCE | 0
2 | RESERVOIR/TANK | 0
3 | TRANSMISSION | 0
4 | DISTRIBUTION | 0
5 | ELECTROMECHANICAL | 0
| SUB-TOTAL 1 | 0
| ADD 18% VAT | 0
| GRAND TOTAL | 0

## Borehole and Source
Community Tap stand (CTS) Project to be constructed in Leteruwa Community in Kaabong District
BILL NO. 1 BOREHOLE SOURCE
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
1 | BOREHOLES AND BOREHOLE SOURCE
1.1 | Galvanised Mild Steel (GMS) pipes with threaded joints, all to BS 3601, not in trench and of the following sizes:
1.1.1 | ND50mm(2") ND Transmision line | m | 10 |  | 0
1.1.2 | ND50mm(2") ND for Pump wash out | m | 2 |  | 0
1.1.3 | GMS double socketed long radius 90 degrees bends to BS 3601 of 50mm(2") ND | nr | 1 |  | 0
1.1.4 | GMS socketed bends 45 degrees 50(2")mm ND | nr | 2 |  | 0
1.1.5 | Double socketed brasss gate valves to BS 5150 for operation by hand, to ND 50 mm(2") | nr | 2 |  | 0
1.1.6 | Socketed GMS Non-Return Valve to ISO 2441 to PN 10 for ND 50mm(2") | nr | 1 |  | 0
1.1.7 | Socketed Pressure Gauge N30 Series for ND 25mm(1") | nr | 1 |  | 0
1.1.8 | Socketed Air valve ND 25mm(1") | nr | 1 |  | 0
1.1.9 | GMS Equal Tee ND 50x50x50mm (2x2x2") | nr | 1 |  | 0
1.1.10 | GMS Reducing Tee ND 50X50X25mm(2x2x1") | nr | 2 |  | 0
0
1.1.11 | GMS Reducing Socket ND50x40mm(2X1½") | nr | 1 |  | 0
0
1.1.12 | GMS ND 5Omm(2") Nipple | nr | 6 |  | 0
0
1.1.13 | GMS ND 40mm(1½") Nipple | nr | 1 |  | 0
0
1.1.14 | GMS ND 25mm(1") Nipple | nr | 1 |  | 0
0
1.1.15 | GMS ND50mm(2") socketed union | nr | 2 |  | 0
0
1.1.16 | GMS ND 50mm(2") Elbow | nr | 2 |  | 0
0
1.1.17 | GMS ND 50mm(2") Soceket | nr | 3 |  | 0
1.1.18 | Supply,Install and do Welding of the third plate as well cover for the borehole and all its accessories for the purpose of securing the pump and all installations in the well (the client has the third plate) | nr | 1 |  | 0
1.2.0 | BUILDING WORKS
1.2.1 | Construct a chain linked fence; 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of galvanised barbed wire gauge 10 on top, anchored into blockwork dwarf wall as per drawings number 2(Page 2 of 2), height 2.075m | M | 38 |  | 0
1.2.2 | Supply and fix gate to BS 3470, painted to Engineer's approval, of 2X2.075M as per attached detailed drawing number 2 (Page 2 of 2) and Provide heavy duty pud lock(Mindy Guard-Medium Size 50mm) for the gate | Item | 1 |  | 0
1.2.3 | Plant paspalum grass in the compound of pump intake and provide watering during time of construction. See detailed drawings number 2( page 1 of 2) | m² | 24.39 |  | 0
1.3.0 | Earth Works
Excavation of Foundation
1.3.1 | Excavation for pad foundations in soft/rock material commencing from relatively horizontal ground level to a minimum depth of 800mm | m³ | 2.646 |  | 0
1.3.2 | Selected excavated material other than top soil or rock backfilled and compacted to sides of foundations | m³ | 1.6117 |  | 0
1.4.0 | Insitu Concrete incl. Placing
1.4.1 | Provision and placing of concrete, design mixes to BS 5328 with Oridnary portland cement to BS 12 or BS 146 and aggregate 10mm dia mahine crushed to the following grade:
1.4.2 | Concrete class 15; Blinding | m³ | 0.16632 |  | 0
1.4.3 | Concrete Class 25: 600x600x250mm thick Pad footing | m³ | 0.8316 |  | 0
1.4.4 | Concrete Class 25:250x250mm stub Column | m³ | 0.63525 |  | 0
1.4.5 | Concrete Ancilliaries
1.4.5.1 | Formwork - fair finish to pad footing and stub column | m | 38.4 |  | 0
1.4.6 | Reinforcement in concrete
1.4.6.1 | Steel fabric reinforcement to BS4483 , fabric reference A252, and of the following mass
1.4.6.2 | T-10 bars (Nominal mass 0.5-2 kg/m) | kg | 51.744 |  | 0
1.4.6.3 | Supply and spread a 50mm layer of machine crushed aggregates in the fenced area. | item | 1 |  | 0
1.4.7 | Sundries
1.4.7.1 | Binding Wire (2mm diam) | Kg | 2.5 |  | 0
1.4.7.2 | Assorted nails | Kg | 4 |  | 0
1.5.0 | Inspection Chamber
1.5.1 | Construct a reinforced concrete meter chamber 1.5x1.5m as detailed in drawings, with vents to specs and a precast reinforced concrete cover raising 300mm above ground, to protect the Bulk meter, Valves and flash out connection, including all earthwork, placing of concrete works and installation of plumbing fittings. Provide a top sleeve to protect the ND50mm GMS pipes at wall crossing with the chamber. | item | 1 |  | 0
1.5.2 | Anchorage
1.5.2.1 | Cast 300x300mm anchorage concrete block using C30 concrete, around the ND50mm GMS pipe at the Manhole as protection against vibration. | Item | 1 |  | 0
1.6 | Riser Pipe and Pump Installation
1.6.1 | Motor cable (water resistent Cable), 6 mm² - 3-phase cable for power and 1-phase cable for ground | m | 0 |  | Rate only
1.6.2 | Heavy duty white column Upvc pipes riser pipe ND50mm PN10 of square threads, 6.4mm min. thickness and able to withstand 35kg/sq cm | nr | 15 |  | 0
1.6.3 | Provide a safetyline(A polypropylene rope or a stainless steel braided cable) for future maintenance of the pump | m | 50 |  | 0
1.7 | Platform Construction
1.7.1 | Supply and cast a telescopic pedestal in concrete mix 1:2:4, as detailed in the drawings and specification. | item | 1
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Reservoir
Community Tap stand (CTS) Project to be constructed in Leteruwa Community in Kaabong District
BILL NO.2 8000LITRES RESERVOIR/PLASTIC TANKS
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
2 | Element NO.1: Substructure
2.1 | Site Preparation
2.1.1 | Excavate over site to reduced levels commencing from stripped site level | m² | 36 |  | 0
2.1.2 | Dig out any existing termite mount, destory queen and apply approved anti-termite spray to the entire site | m² | 81 |  | 0
2.1.3 | Anti- termite treatment to sides and bottoms of foundation | m² | 28 |  | 0
2.1.4 | Ditto but stripped surfaces of the ground | m² | 7.84 |  | 0
2.1.5 | Ditto but blinded surface of hardcore | m² | 7.84 |  | 0
2.2 | Trees
2.2.1 | Cut and dispose of trees of the following girth; include removal of stump
2.2.2 | Girth 500mm - 1000mm (0.5m-1m) | nr | 1 |  | 0
2.2.3 | Girth 1m - 2m | nr | 1 |  | 0
2.3 | Stumps
2.3.1 | Remove and dispose of stumps of the following diameter; include for grabbing up the roots and backfilling the hole left with top soil
2.3.2 | Diameter 150mm - 500mm | nr | 1 |  | 0
2.3.3 | Diameter 500mm - 1m | nr | 1 |  | 0
2.4 | Earthworks and Excavation |  |  |  | 0
2.4.1 | Excavate foundation trench not exceeding 1.5m deep commencing from reduced level | m³ | 7.5 |  | 0
2.4.2 | Ditto but column bases | m³ | 6 |  | 0
2.4.3 | Extra over excavations: breaking up rock met with in excavations | m³ | 0.8 |  | 0
2.5 | Disposal of excavated materials
2.5.1 | Return, fill in and ram selected excavated material around the foundation around foundations and walling; placed in 200mm layers, watered and compacted to 95% MDD | m³ | 8.5 |  | 0
2.5.2 | Load, wheel and evenly spread out surplus soil on site | m³ | 5.8 |  | 0
2.6 | Fillings
2.6.1 | 125mm murram filling: well watered and compacted to 95% MDD 95%: to make up levels under floor bed | m² | 6.6 |  | 0
2.6.2 | 150mm Hardcore bed: in broken stone well compacted, consolidated and blinded with and including 20mmlayer of lake/river sand well watered ready to receive concrete | m² | 6.6 |  | 0
2.6.3 | Excavation for pad foundations in soft/rock material commencing from relatively horizontal ground level to a minimum depth of 800mm | m³ | 1.62 |  | 0
2.6.4 | Selected excavated material other than top soil or rock backfilled and compacted to sides of foundations | m³ | 1.61 |  | 0
Insitu Concrete incl. Placing
2.6.5 | Provision and placing of concrete, design mixes to BS 5328 with Oridnary portland cement to BS 12 or BS 146 and aggregate 10mm dia machine crushed to the following grade:
2.6.5.1 | Concrete class 15; Blinding to pad bases | m³ | 0.11088 |  | 0
2.6.5.2 | Concrete Class 25: 600x600x250mm thick Pad footing | m³ | 0.5544 |  | 0
2.6.5.3 | Concrete Class 25:250x250mm stub Column | m³ | 0.385 |  | 0
Concrete Ancilliaries
2.6.6 | Formwork - fair finish to pad footing and stub column | m2 | 25.6 |  | 0
2.7 | Concrete to foundation trenches
2.7.1 | Mass concrete mix 1:4:8/38mm aggregate; 50mm thick blinding to foundations | m² | 3.542 |  | 0
2.7.2 | Mass concrete mix 1:3:6/20mm aggregate, in foundation trenches | m³ | 2.7412 |  | 0
| Reinforced concrete in mix 1:1.5:3/20mm aggregate vibrated in: |  |  |  | 0
2.7.3 | Column and Column Base [Plinth Structure] | m³ | 2.926 |  | 0
| Ditto to ground beam | m³ | 1.386 |  | 0
2.8 | Sawn Form work
2.8.1 | Sawn formwork to ground beam | m² | 26.4 |  | 0
2.9 | Reinforcement
2.9.1 | Mild steel bar reinforcement to BS 4483
2.9.2 | 8mm bars(shear reinforcement to column) | Kg | 48 |  | 0
2.9.3 | 8mm bar as a chair/spacer for the column base | Kg | 2 |  | 0
2.1 | High yield tensile steel bar reinforcement to BS 4461 as described including cutting to lengths, bending, hoisting and fixing including all the ncessary binding wire and chair/ spacer blocks
2.10.1 | 16mm bars | Kg | 176.8704 |  | 0
2.10.2 | 10mm bars for ground beam | Kg | 32.5776 |  | 0
2.11 | Sawn Form work
2.11.1 | Ditto but Columns | m² | 19.504 |  | 0
2.12 | Foundation/Plinth Walls
2.12.1 | Hard burnt clay bricks to BS 3921(3.5N/mm² compressive strength) bedded and jointed in cement and sand(1:3) mortar
2.12.2 | 230mm wall | m² | 7.28 |  | 0
2.13 | Damp Proof Membrane
2.13.1 | 1000 Gauge polythene sheet damp proof membrane in one layer with 300mm end laps: laid on blinded hardcore | m² | 6.6 |  | 0
2.13.3 | 230mm wide: APC laid along the main layout of wall | m | 11.2 |  | 0
2.13.4 | DPC | roll | 2 |  | 0
2.14 | Plinth wall finishes
2.14.1 | 15mm cement and sand(1:3) render: steel trowelled smooth | m² | 15.4 |  | 0
2.15 | Element NO.2: Building Frame[Super structure]
2.15.1 | Reinforced in-situ concrete mix 1:1.5:3/20mm aggregate (machine crush-aggregate) in
2.15.2 | Columns | m³ | 2.0529 |  | 0
2.15.3 | Ring beams | m³ | 2.5035 |  | 0
2.15.4 | Slab but concrete mix 1:2:4/20mm aggregate | m³ | 1.78 |  | 0
2.16 | High yield tensile steel bar reinforcement to BS 4461 as described including cutting to lengths, bending, hoisting and fixing including all the ncessary binding wire and spacer blocks
2.16.1 | 16mm bars for columns and ring beam | Kg | 367.9 |  | 0
2.16.2 | 8mm bars(shear reinforcement to column and beams) | Kg | 257.25 |  | 0
2.16.3 | 10mm bars for slabs | Kg | 74.55 |  | 0
2.17 | Sundries
2.17.1 | Binding wires(2mm diameter) | roll | 1 |  | 0
2.17.2 | Assorted Nails | Kg | 15 |  | 0
2.18 | Sawn Form work to: |  |  |  | 0
2.18.1 | Sides and soffites: Beam | m² | 95.76 |  | 0
2.18.2 | Vertical sides: Column | m² | 88.32 |  | 0
2.18.3 | Soffites: Slab | m² | 9.18 |  | 0
2.19 | Element NO.3: Walls |  |  |  | 0
2.19.1 | Provide Eucalyptus poles(75mm/3" to 100mm/4" in size and length between 15 to 20feet) @) as a temporary structure for scaffolding | No. | 20 |  | 0
2.25 | Water Tank and Plumbing System
2.25.1 | Supply and Install Gentex tank of 8000litres plastic tank with a 0.35m steel wide access man way, ball float valve, fixed inlet (50mm diam), outlet (50mm diam ), overflow and washout (50mm dia)GMS pipes connection complete with internal pipe work and fittings, bracings as detailed in the drawings number 1(Page 3 of 11) | Item | 1 |  | 0
2.25.2 | Supply and fix iron sheet gauge 28 prepainted on the four vertical sides of the tank to protect the tank from sun radiation | m² | 8.14 |  | 0
2.25.3 | Supply of foldable ladder
2.25.3.1 | Stainless steel material 304 stainless steel withdth 500mm and height 4000m | nr. | 1 |  | 0
2.26 | Supply and fix galvanised Mild Steel (GMS) pipes with threaded joints, all to BS 3601, not in trench and of the following sizes - Tank WashOut.
2.26.1 | 50mm ND drop down pipe | m | 6 |  | 0
2.26.2 | GMS double socketed long radius 90 degrees bends to BS 3601, flanges to ISO 2441 of ND 50mm(2") | nr. | 2 |  | 0
2.26.3 | All socketed gate valves to BS 5150 for operation by hand, to ND 50 mm(2") | nr. | 1 |  | 0
2.26.4 | Socketed nipples ND 50mm(2") | nr. | 2 |  | 0
2.26.5 | Socketed connecting Union/ connector ND50mm(2") | nr. | 2 |  | 0
2.26.6 | HDPE PN6 ND OD63 X 2" Female adapters | nr. | 1 |  | 0
2.27 | Supply and fix galvanised Mild Steel (GMS) pipes with threaded joints, all to BS 3601, not in trench and of the following sizes - rising main.
2.27.1 | ND50mm(2") ND Transmision line | m | 8 |  | 0
2.27.2 | GMS double socketed long radius 90 degrees bends to BS 3601 of 50mm(2") ND | nr | 2 |  | 0
2.27.3 | GMS straight socket ND50(2")mm | nr | 2 |  | 0
2.27.4 | GMS ND50mm(2") socketed union | nr | 2 |  | 0
2.27.5 | Socketed GMS ND 50mm(2") long screw fitted with a bucknut | nr | 1 |  | 0
2.28.0 | Fencing
2.28.1 | Construct a chain linked fence; 100x100mm Concrete post of C25 concrete and wire galvanised wire chain link fence of gauge 10 to BS 1722, with triple row of galvanised barbed wire gauge 10 on top, anchored into blockwork dwarf wall as per drawings number 2(Page 2 of 2), height 2.075m | M | 38 |  | 0
2.28.2 | Supply and fix gate to BS 3470, painted to Engineer's approval, of 2X2.075M as per attached detailed drawing number 2 (Page 2 of 2) and Provide heavy duty pud lock(Mindy Guard-Medium Size 50mm) for the gate | Item | 1 |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Electro-Mechananical
Community Tap stand (CTS) Project to be constructed in Leteruwa Community in Kaabong District
BILL NO.3 ELECTROMECHANICAL
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
ELECTRO-MECHANICAL WORKS
Submersible pump
NB. Contractors are to quote for Lorentz pump of PS2 - 1800C-SJ5-12 series of Max flow rate of 7.6m3/hr and Max.head; total head (H) of 70m; with Controller PS- 4000, Max.Power of 1.8KW. During construction. A Pump and PV sizing shall be done and PS2-4000 pump that shall be selected for a particular site, shall not exceed the characteristic(Flow rate and Head) mentioned. Further, Contractors are also to quote for Lorentz PV panels of Peak Power(P max) of 200Wp, Maximum number of Solar Panels to be installed is 10. The well casing, internal is 5 inches
3.1.1 | Lorentz pump as PS2-1800C-SJ5-12 series Pumpset Q = 7.6m3/hr(Max.), H = 70m(Max.) total head, with controller PS-4000, Max. power of 1.8KW with a high efficiency EC Drive Brushless Motor; Model Lorentz ECDRIVE 4000-HRE, rated Power 1.8kw and Motor cable of 6mm2 for 50m. Refer to the PV drawings attached | nr | 1 |  | 0
ELECTRICAL WORKS
Solar PV System
3.1.2 | Lorentz PV as LC200-Portable Kit, Polycrystalline Solar Panels, @200Wp, 8.84Imp, 37.3 Vmp, See details in PV and Pump Sizing Report attached | nr | 6 |  | 0
3.1.3 | PV Disconnect 400 - 50- 3-s box connection with DC Disconnect Switch and Lightning surge protection with maximum voltage of 400V DC and maximum current of 50A, See details in PV and Pump Sizing report | nr | 1 |  | 0
| Solar Mounting Structure |  |  |  | 0
3.1.4 | Solar Array mounting frame for 10no. Solar panels each measuring 1956x992mm, to be fabricated using galvanised rust-free/resistant steel metal supported by galvanised steel pipes/angle sections onto a reinforced concrete base constructed to specifications. Special bolts and nuts with arren-keys shall be supplied for fastening modules, enhanced for theft-proof and spot welded, Ref drawing GKA [- -]12, RCT-GKA [- -]03 & 04, RCT-GKA [- -]01 & 02 and RCT-GKA [- -] 05) attached. | item | 1 |  | 0
3.1.5 | Surge protectors2 (See details in PV & Pump sizing report attached) | nr | 1 |  | 0
0
3.1.6 | Supply and fix a 3G PS-Communicator compartible with PS2 Pumps |  | 1 |  | 0
3.1.7 | Well Probe V2 ( see details in PV & Pump Sizing report attached) | nr | 1 |  | 0
3.1.8 | Pressure switch (See details in PV & Pump sizing report attached) - provide all the necessary connections and high pressure ball valve at the reservoir and install the pressure switch to the satisfaction of the engineer onsite. | Item | 1 |  | 0
3.1.9 | Assortment of electrical cables, interconnects and accessories for complete system wiring, including where necessary, underground cables, wired in full conduit technique; supplied and installed to specifications. | sum | 1 |  | 0
Wiring, Riser Pipe and Pump Installation
3.1.10 | Motor cable (water resistent Cable), 6mm² | m | 0 |  | 0
3.1.11 | PPR riser pipe ND50mm(1½") PN10 | nr | 0 |  | 0
3.1.12 | Stainless steel adaptor set ND50mm(1½") | set | 2 |  | 0
3.1.13 | Provide a safetyline(A polypropylene rope or a stainless steel braided cable) for future maintenance of the pump | m | 50 |  | 0
Earthing and Lightening Protection
3.1.14 | Complete with copper rod 16mm² earth wire , copper wire, copper clamp, charcoal, damp salt for earthing . Ligtening complete with copper rod, copper tape , copper spike , copper bolt at the solar structure | nr | 1 |  | 0
Water Monitoring system
3.1.15 | Bulk Meter, WP Water meter DN50mm(2"), See details in the PV & Pump Sizing report attached (Page 21-23 of 31 of the combined drawings) | nr | 1 |  | 0
| Carried to Summary |  |  |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Transmission main
Community Tap stand (CTS) Project to be constructed in Leteruwa Community in Kaabong District
BILL NO.4 DISTRIBUTION SYSTEM
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
4 | DEMOLITION AND SITE CLEARANCE
4.1 | General Site Clearance
4.1.1 | General site clearance for pipe trench | m2 | 120 |  | 0
4.2 | PE pressure pipes to ISO 4427, PN10 and fittings conforming to BS 12201, all to PN 10, laid in trench to a depth n.e 1.5m. Rate should include cost of fittings (connectors), excavation, laying and backfilling of trench
4.2.1 | OD50mm PE PN10 | m | 397 |  | 0
4.3 | PE Straight Couplers - PN10
4.3.1 | OD50mm | nr | 6 |  | 0
4.5 | PE Adapter - PN10
4.5.1 | OD50X 2" Female adapters | nr | 1 |  | 0
4.5.2 | OD50 X 1½" Male adapters | nr | 0 |  | 0
| Air Release Valve |  |  |  | 0
4.5.3 | Supply and install a 50mmOD air release valve with all its fittings,along the PN6 pipeline, well secured by 230mm thick,1000x1000mm masonry manhole, well finished and covered with a reinforced concrete cover cast insitu using 10mm rebars at 150mm spacing, to be constructed in consultation with the GOAL Engineer onsite. | nr | 1 |  | 0
4.6 | Marker posts
4.6.1 | Marker post for pipelines as per drawings. Painted white and writing painted black. This should be provided every 200m. | nr | 2 |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0

## Distribution main
Community Tap stand (CTS) Project to be constructed in Leteruwa Community in Kaabong District
BILL NO.5 DISTRIBUTION SYSTEM
ITEM NO. | DESCRIPTION | UNIT | QTY | RATE (USHS.) | AMOUNT (USHS.)
NB: Contractors Should note that there is going to be no provision for construction a a Public Tap stand/Standpipe. Only a meter chamber shall be constructed. Distribution pipe ending after the meter chamber to be fitted with a Female Adapter(PE) and pluged with End Cap(PE)
5.1 | DEMOLITION & SITE CLEARANCE
5.1.1 | General clearance along pipeline | m2 | 356 |  | 0
5.2 | Plastic PE pressure pipes to BS 5114 OR its equivalent, all to PN6 and fittings all to PN 10, laid in trench to adepth n.e 1.5m. Rate should include cost of excavation, laying and backfilling of trench
5.2 | PE Pressure Pipes
5.2.1 | OD40mm | m | 800
5.2.2 | ND 50mm GI class C | m | 5 |  | 0
5.2.3 | OD50mm HDPE PN6 | m | 85
5.2.4 | ND 32mm GI class C for crossing river of width 9m | m | 9
5.2.5 | OD32mm | m | 300 |  | 0
5.3 | PE Straight Coupling - PN10
5.3.1 | OD40mm | nr | 4 |  | 0
5.2.3 | OD50mm | nr | 3
5.3.2 | OD32mm | nr | 5 |  | 0
5.4 | PIPEWORK-FITTINGS AND VALVES
5.4.1 | HDPE Tee
5.4.2 | Reducing Tee - PN6
5.4.2.1 | 40x32 mm OD | nr. | 1 |  | 0
5.4.3 | Reducing Connector - PN6
5.4.3.1 | 40X32mm OD | nr. | 2 |  | 0
5.4.3.2 | 50x40mmOD | nr. | 3 |  | 0
5.4.4.0 | PE Adaptor
5.4.4.1 | Male Adaptor
5.4.5.1 | 40mmOD | nr | 3 |  | 0
5.4.6.0 | PE End Cap
5.4.6.1 | 32mm OD | nr. | 3 |  | 0
5.5.0 | Air Release Valve
5.5.1 | Supply and install a 40mmOD air release valve with all its fittings,along the PN6 pipeline, well secured by 230mm thick,1000x1000mm masonry manhole, well finished and covered with a reinforced concrete cover cast insitu using 10mm rebars at 150mm spacing, to be constructed in consultation with the GOAL Engineer onsite. | nr. | 3 |  | 0
| Collection 1 to Summary |  |  |  | 0
5.6.1 | Marker post for pipelines as per drawings Number 3 (Page 1 of 1). Painted white and writing painted black | nr. | 5 |  | 0
5.6.2 | Construct a reinforced concrete meter chamber with a precast reinforced concrete concrete cover raising above the ground level by 300m as in the drawing number 5 (Page 1 of 1) including all earthwork, concrete works, plumbing, all relevant fitings( Gate Valve, meter,etc.); galvanized iron pipe and fitting all to PN 6 | nr | 3 |  | 0
| Collection 2 to Summary |  |  |  | 0
5.6.1 | Page 1: Collection 1 to Summary |  |  |  | 0
5.6.2 | Page 2: Collection 2 to Summary |  |  |  | 0
| TOTAL TO GRAND SUMMARY |  |  |  | 0