## Cover
GOAL UGANDA
Construction of Busolo Piped water scheme extension in Bugiri District

## Preamble
GOAL UGANDA
EXTENSION OF BUSOLO PIPED WATER SCHEME IN BUGIRI DISTRICT
Preamble: This BoQ relates to the proposed construction of Busolo piped water supply scheme extensions in Bugiri District. The BoQ should be read together with the drawings and the technical specifications. The major system components; construction of intake & reservoir works, and laying of the transmission & distribution network have been completed. The successful contractor shall be expected to connect, lay below ground and cover the extension pipeline, supply & install isolation valves, Air release valves and Washouts at selected points. The project has allowed for 15 PSPs for water collection however, the contractor shall be required to construct the service pipes to the PSP location and, terminate after the Manholes. GOAL Uganda does envisage an admeasured contract; were final quanitities shall be determined onsite after construction

## Grand Summary 1
GOAL UGANDA
EXTENSION OF BUSOLO PIPED WATER SCHEME IN BUGIRI DISTRICT
ENGINEER'S ESTIMATE
GRAND SUMMARY I
Bill No | Bill Description | INVESTMENT COST
GENERAL
BUS G | GENERAL ITEMS | 0
| SUB-TOTAL | 0
BUSOLO PIPED WATER SCHEME NETWORK EXTENSION
BUS-EXT | NETWORK EXTENSION | 0
| CONSUMER CONNECTIONS | 0
| Sub-Total 1 | 0
| Allow for 18% VAT | 0
| TOTAL | 0

## General
GOAL UGANDA
EXTENSION OF BUSOLO PIPED WATER SCHEME IN BUGIRI DISTRICT
DESCRIPTION: | GENERAL ITEMS
ITEM NO. | ITEM DESCRIPTION | UNIT | QTY | RATE | AMOUNT
|  |  |  | Ushs | Ushs
METHOD RELATED CHARGES
BUS G-1 | Mobilisation on site | sum | 1
BUS G-2 | Demobilise on completion of the Works | sum | 1
BUS G-3 | Supply and/or erect Contractor's site offices. | sum | 1
BUS G-4 | Maintain Contractor's site offices, including all services | months | 6
BUS G-5 | Remove Contractor's site offices on completion of the Works | sum | 1
SPECIFIED REQUIREMENTS
Equipment for use by the Engineer's staff
BUS G-6 | Use of Contractor's surveying equipment by the Engineer | Days | 2 |  | 0
BUS G-7 | Provision of services of 1No survey chainmen | months | 1 |  | 0
Testing of the works
BUS G-8 | Pressure testing and sterilization of the constructed pipe network: nominal bore not exceeding 300mm; maximum test pressure not exceeding 1.5 the pipe's pressure rating to Engineer's satisfaction. | km | 6 |  | 0
BUS G-9 | Testing of pressure pipes at Uganda Natioal Bureau of Standards: 32 to 50mmOD | sum | 1 |  | 0
Miscellaneous
BUS G-10 | Prepare ''As-Built'' or Record drawings as per specifications of installations, Asset Register and Operation and Maintenance Manual all bound in hard cover for the Engineer's approval and submission to the Employer (3 copies shall be required inclusive of editable versions) | Sum | 1 |  | 0
| Total for General Items Carried to Summary |  |  |  | 0

## Network extension
GOAL UGANDA
EXTENSION OF BUSOLO PIPED WATER SCHEME IN BUGIRI DISTRICT
BILL No. | BUS-EXT
DESCRIPTION: | NETWORK EXTENSION
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Preamble:
The works under this bill are covered under Part 2 of the Particular Specifications.
DEMOLITION AND SITE CLEARANCE
General Site Clearance
BUS-EXT1 | General site clearance for pipe route | m2 | 7900 |  | 0
PIPEWORK-PIPES
Ductile Iron Pressure Pipes
Ductile Iron pressure pipes to BS3505, BS4346 , DN 40mm; connected to HDPE pipes at four sections - rate to include flanged adaptors and associated fittings
BUS-EXT2 | Not in trenches (Anchored on rocks) | m | 80 |  | 0
Allow for Plastic Pressure Pipes- Distribution - Sleeve pipes provided at road crossing and for all pipes passing through the wall
HDPE pressure pipes to BS 3505, include straight connectors, all to PN 10, of pipes of the following sizes, laid and backfilled in trench to adepth n.e 1.5m
BUS-EXT3 | OD50mm | Rolls | 4 |  | 0
BUS-EXT4 | OD40mm | Rolls | 60 |  | 0
BUS-EXT5 | OD32mm | Rolls | 2 |  | 0
HDPE pressure pipes to BS 3505, include straight connectors, all to PN 16, of pipes of the following sizes, laid and backfilled in trench to adepth n.e 1.5m
BUS-EXT6 | OD50mm | Rolls | 3 |  | 0
BUS-EXT7 | OD40mm | Rolls | 12 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-FITTINGS AND VALVES
Make a connection for OD 40 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (Saddle clamp, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of following pipes and respective sizes. All fittings to a pressure rating of PN16
BUS-EXT8 | OD 140mm UPVC | nr | 1 |  | 0
BUS-EXT9 | OD 125mm UPVC | nr | 1 |  | 0
BUS-EXT10 | OD 110mm UPVC | nr | 1 |  | 0
BUS-EXT11 | OD 90mm PE | nr | 1 |  | 0
BUS-EXT12 | OD 50mm PE | nr | 2 |  | 0
Make a connection for OD 50 HDPE, complete as in drawings, inclusive of excavation, backfill, fittings (Saddle clamp, Flanged adaptors, Gate valves, thrust blocks, surface box etc) for connection to the distribution main of following pipes and respective sizes. All fittings to a pressure rating of PN16
BUS-EXT13 | OD 110mm UPVC | nr | 1 |  | 0
Make a connection for OD32HDPE, complete as in drawings, inclusive of excavation, backfill, plumbing fittings (A DN 32mm Saddle clamp assembly, Gate valves, water meters, adapters, GI plug etc) for connection to the distribution main of HDPE pipes for the following pipe sizes. All fittings to a pressure rating of PN16. Provide sleeve pipes at manhole crossing to protect the pipes
BUS-EXT14 | OD 90mm PE | nr | 5 |  | 0
BUS-EXT15 | OD 75mm PE | nr | 5 |  | 0
BUS-EXT16 | OD 63mm PE | nr | 2 |  | 0
BUS-EXT17 | OD 50mm PE | nr | 2 |  | 0
BUS-EXT18 | OD 40mm PE | nr | 2 |  | 0
End caps
Compression HDPE end caps to fit HDPE spigots, to ISO 161 and to PN 16 of the following spigot sizes
BUS-EXT19 | 32mmOD | nr | 15 |  | 0
BUS-EXT20 | 40mmOD | nr | 8 |  | 0
BUS-EXT21 | 50mmOD | nr | 1 |  | 0
Gate Valves: Hand Operated
Supply and install all flanged; 63mm ND CI gate valves (2.5") to BS 5150, flanges to BS 4505, all to PN 16 for operation by tee key, with extension spindle not exceeding 1.5 metres long, installed to pipes of the following sizes. Rate to include equivalent flanged PE adapters to PN16
BUS-EXT22 | 75mmOD PE pipes | nr | 3 |  | 0
Supply and install all flanged; 75mm ND CI gate valves (3") to BS 5150, flanges to BS 4505, all to PN 10 for operation by tee key, with extension spindle not exceeding 1.5 metres long, installed to pipes of the following sizes. Rate to include equivalent flanged PE adapters to PN10
BUS-EXT23 | 90mmOD PE pipes | nr | 3 |  | 0
BUS-EXT24
Supply and install all flanged; 100mm ND CI gate valves (4") to BS 5150, flanges to BS 4505, all to PN 10 for operation by tee key, with extension spindle not exceeding 1.5 metres long, installed to pipes of the following sizes. Rate to include equivalent flanged adapters to PN10
BUS-EXT25 | 110mmOD UPVC pipes | nr | 1 |  | 0
Supply and install all flanged; 50mm ND CI gate valves (2") to BS 5150, flanges to BS 4505, all to PN 16 for operation by tee key, with extension spindle not exceeding 1.5 metres long, installed to pipes of the following sizes. Rate to include equivalent flanged adapters to PN16
| 63mmOD PE pipes | nr | 1 |  | 0
Supply and install all flanged; 40mm ND CI gate valves (1.5") to BS 5150, flanges to BS 4505, all to PN 10 for operation by tee key, with extension spindle not exceeding 1.5 metres long, installed to pipes of the following sizes. Rate to include equivalent flanged PE adapters to PN10
BUS-EXT26 | 40mmOD PE pipes | nr | 1 |  | 0
Air Valves
Flanged anti shock, anti surge double air valve, 75 mm ND, as specified, flanges to ISO 2441, complete with isolating gate valve to ISO 7259, flange on socket tee, thrust blocks, distance pieces, all to PN 16, as specified and all fittings necessary to make the connection complete; for the following pipe sizes
BUS-EXT27 | 110 mmOD UPVC | nr | 3 |  | 0
BUS-EXT28 | 75mmOD PE | nr | 1 |  | 0
Junctions and Branches
All flanged tee to BS 4346, flanges to BS 4504, all to PN 16, and of the following sizes
BUS-EXT29 | ND75/75mm | nr | 1 |  | 0
Washouts
Type 2 Washout as specified in the drawings, complete with CI Tee, adaptors, drainage pipes, CI gate valve, CI flap valve, surface boxes, thrust blocks, 100m PE down pipe, and all other fittings necessary to make the complete installation on pipes of the following sizes; all to PN16
BUS-EXT30 | 75mmOD | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
Crossings
Open Channels
Unlined open channels crossings for pipes of the following sizes
BUS-EXT31 | Not exceeding 300 mm ND | nr | 1 |  | 0
Reinstatement
Roads
Breaking up, temporary and permanent reinstatement of murram roads for the following pipe sizes
BUS-EXT32 | Not exceeding 300 mm ND | m | 18 |  | 0
PIPEWORK-SUPPORTS AND PROTECTION, ANCILLARIES TO LAYING AND EXCAVATION
Extras to Excavation and Backfilling
In Pipe Trenches
Extras to excavation in pipe trenches in the following materials
BUS-EXT33 | In rock | m³ | 165.9 |  | 0
Concrete Stools and Thrust Blocks
Thrust Blocks
Mass concrete grade C15 thrust blocks for pipes and fittings, volume 0.2-0.5 m³, for the following pipe sizes
BUS-EXT34 | Diameter not exceeding 300 mm ND | nr | 5 |  | 0
Surrounds
Pipe surrounds, of mass concrete , for the following pipe sizes
BUS-EXT35 | Diameter not exceeding 200 mm ND | m | 100 |  | 0
PIPEWORK-MANHOLES AND PIPEWORK ANCILLARIES
BUS-EXT36 | Construct a 200mm thick 1000x1000mm chambers with a 200mm thick clay burnt bricks and precast reinforced concrete cover raising above the ground level by 300mm as detailed in the drawing ). Provide a 2"PVC pipe as top sleeve to protect the pipes at wall crossing of the chamber. The chamber cover should be finished smooth. | nr | 15 |  | 0
BUS-EXT37 | Ditto but as protection to the service valves installed in the system | nr | 11 |  | 0
Other Pipework Ancillaries
Marker Posts
BUS-EXT38 | Marker posts for gate valves | nr | 11 |  | 0
BUS-EXT39 | Marker posts for Washout | nr | 1 |  | 0
BUS-EXT40 | Marker posts for pipes @ 200M spacing | nr | 50 |  | 0
Lighting at the Reservoir site
| Supply and install double solar powered lighting system complete, with light unit on 6m-GI poles to the approval of the supervising Engineer. | nr | 1 |  | 0
|  |  |  | Carried to Collection | 0
COLLECTION
| Collection, Page H-W-7/1 |  |  |  | 0
| Collection, Page H-W-7/2 |  |  |  | 0
| Collection, Page H-W-7/3 |  |  |  | 0
Carried to Summary |  |  |  |  | 0

## Connections
GOAL UGANDA
EXTENSION OF BUSOLO PIPED WATER SCHEME IN BUGIRI DISTRICT
BILL No. | BUS-C
DESCRIPTION: | CONSUMER CONNECTIONS
ITEM NO. | ITEM DESCRIPTION | UNIT | QUANTITY | RATE | AMOUNT
|  |  |  | UShs | UShs
Saddle Clamps
uPVC saddle clamps, to BS 4772, all to PN16, to the following sizes
BUS-C1 | 140X32mmOD | nr | 30 |  | 0
BUS-C2 | 125X32mmOD | nr | 30 |  | 0
BUS-C3 | 110X32mmOD | nr | 30 |  | 0
Plastic Pressure Pipes
HDPE pressure pipes to BS 3505, include straight connectors, all to PN 10, of pipes of the following sizes, laid and backfilled in trench to adepth n.e 1.5m
BUS-C4 | OD32mm | Rolls | 10 | 0 | 0
Note:
All fittings are to be approved by the Engineer.
Carried to Summary |  |  |  |  | 0